## Prioritization of Repairs
PRIORITIZATION OF REPAIRS MATRIX
| OJUA | 2007 NESC
Item | Deviation Code | Section | Code |  | Page | General Description | A | B | C | Exceptions | NOTES
1 | PG | 9 | 092 | C | 18 | Messenger Wires and guys (Grounding) | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
2 | PG | 9 | 094 | B2 | 23 | Driven rods | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
3 | PG | 12 | 123 | A | 39 | Protective Grounding or physical isolation of non-current-carrying metal parts | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) | Also see 092C (page 18)
4 | AB | 21 | 214 | B | 71 | Lines or Poles Permanently abandoned | Conditions that could reasonably be expected to endanger life or property | Almost Always | Never | None | Also see 012C (page 1)
5 | PG | 21 | 215 | C2 | 72 | Anchor guys and span guys shall be effectively grounded | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
6 | MV | 21 | 215 | C5 | 72 | Use of insulators in anchor guys, span guys and span wires supporting luminaries or traffic signals | Conditions that could reasonably be expected to endanger life or property | Almost Always | Never | Yes (see code)
7 | MS | 21 | 215 | C5 Exception | 72 | Anchor guys and span guys not insulated | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
8 | PV | 21 | 217 | A2 | 73 | Readily climbable support structures or tree | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
9 | DB | 21 | 217 | C | 74 | Protections and marking of guys | Never | Always | Never | Yes (see code)
10 | MS | 21 | 217 | C | 74 | Protections and marking of guys | Never | Always | Never | Yes (see code)
11 | PH | 23 | 231 | A | 85 | Clearances of supporting structures (Fire Hydrants) | Never | If no agreement | Mostly with agreement | Yes (see code)
12 | PH | 23 | 231 | B | 86 | Horizontal clearances of supporting structures | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | None
13 | PS | 23 | 231 | B | 86 | Clearances of supporting structures (anchors) | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | None
14 | PV | 23 | 231 | B | 86 | Vertical clearances of supporting structures | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | None
15 | MV | 23 | 232 | Table 232-1 (1) | 92 | Railroad Tracks | Conditions that could reasonably be expected to endanger life or property | Almost Always | Never | Yes (see code) This covers railroads of 22.3' and 24' clearance
16 | MV | 23 | 232 | Table 232-1 (10) | 93 | Roads where it is unlikely vehicles will be crossing under line | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
17 | MV | 23 | 232 | Table 232-1 (2) | 92 | Roads, streets & areas subject to truck traffic | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | None This covers roads with 16' and 15.5' road clearance
18 | BV | 23 | 232 | Table 232-1 (3) | 92 | Driveways, parking lots and alleys | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) Exception 7 (page 94)
19 | MV | 23 | 232 | Table 232-1 (3) | 92 | Driveways, parking lots and alleys | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) Exception 7 (page 94)
20 | BV | 23 | 232 | Table 232-1 (5) | 92 | Areas subject to pedestrian or restricted traffic where there is a 12' pedestrian clearance | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) Exception 8a and 8c (page 94)
21 | MV | 23 | 232 | Table 232-1 (5) | 92 | Areas subject to pedestrian or restricted traffic where there is a 12' pedestrian clearance | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) Exception 8a and 8c (page 94)
22 | BV | 23 | 232 | Table 232-1 (5) | 92 | Areas subject to pedestrian or restricted traffic where there is a 9.5' pedestrian clearance | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | None
23 | MV | 23 | 232 | Table 232-1 (5) | 92 | Areas subject to pedestrian or restricted traffic where there is a 9.5' pedestrian clearance | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | None
24 | PV | 23 | 232 | Table 232-2 (1a) | 96 | Rigid overhang (roads, streets and other areas subject to truck traffic) | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | None
25 | PV | 23 | 232 | Table 232-2 (1b) | 96 | Rigid overhang (driveway, parking lots and alleys) | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | None
26 | BV | 23 | 232 | Table 232-2 (1d) | 96 | Rigid overhang (subject to pedestrians or restricted traffic only) | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) | Also see 234J2c (page 117)
27 | MV | 23 | 233 | C | 99 | Vertical clearance between wires, conductors and cables carried on different support structures. | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) | See Table 233-1 (page 106)
28 | MH | 23 | 234 | B1 | 110 | Horizontal clearance from other supporting structures | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
29 | PH | 23 | 234 | B1 | 110 | Horizontal clearance from other supporting structures | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
30 | MV | 23 | 234 | B2 | 111 | Vertical clearance from other supporting structures | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
31 | PV | 23 | 234 | B2 | 111 | Vertical clearance from other supporting structures | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
32 | BD | 23 | 234 | C3 | 112 | Building attachments | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
33 | MV | 23 | 234 | C3d(1)(a) | 112 | Service drop conductors over roofs Not readily accessible (3 ft) | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) | See Table 234-1 (page 125)
34 | BV | 23 | 234 | C3d(1)(a) | 112 | Service drop conductors over roofs Not readily accessible (3 ft) | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) | See Table 234-1 (page 125)
35 | BV | 23 | 234 | C3d(1)(b) | 112 | Service drop conductors over roofs Not readily accessible (18 in) | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) | See Figure 234-2 (page 119)
36 | BH | 23 | 234 | C3d(2) | 113 | 3' any direction from windows, doors….etc. | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
37 | BV | 23 | 234 | C3d(2) | 113 | 3' any direction from windows, doors….etc. | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
38 | MH | 23 | 234 | Table 234-1 (2a) | 126 | Horizontal Sign Clearance | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) | See Figure 234-1(b) (page 118)
39 | MV | 23 | 234 | Table 234-1 (2b) | 126 | Vertical Sign Clearance | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
40 | MH | 23 | 235 | C1(b) | 137 | Horizontal clearance between supply lines and communications (mid span to building) | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Exception 3 (for mid span)
41 | MV | 23 | 235 | C1(b) | 137 | Vertical clearance between supply lines and communications (mid span to building) | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Exception 3 (for mid span)
42 | BH | 23 | 235 | C1(b) | 137 | Horizontal clearance between supply lines and communications (point of attachment) | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Exception 3 (for point of attachment)
43 | BV | 23 | 235 | C1(b) | 137 | Vertical clearance between supply lines and communications (point of attachment) | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Exception 3 (for point of attachment)
44 | BH | 23 | 235 | C1(c) | 137 | Horizontal clearance between communication lines (point of attachment) | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections |  | Also see 235H2 (page 142)
45 | BV | 23 | 235 | C1(c) | 137 | Vertical clearance between communication lines (point of attachment) | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections |  | Also see 235H2 (page 142)
46 | MH | 23 | 235 | C1(c) | 137 | Horizontal clearance between communication lines (mid-span) | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections |  | Also see 235H2 (page 142)
47 | MV | 23 | 235 | C1(c) | 137 | Vertical clearance between communication lines (mid-span) | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections |  | Also see 235H2 (page 142)
48 | MV | 23 | 235 | C2(b) | 138 | Mid-span Clearance (30 inch rule) | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
49 | PV | 23 | 235 | H1 | 142 | Spacing between communication messengers less than 12" (except by agreement) | Never | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
50 | PV | 23 | 235 | Table 235-6 | 151 | 40" Rule | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections
51 | PC | 23 | 236 |  | 158 - 161 | Climbing space | Never | Not accessible by other means | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections 6. Accessible by other means | Yes (see code)
52 | PV | 23 | 238 | C | 163 | Span wires or brackets carrying luminaries or traffic signals | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code) | See Table 238-2 (page 164)
53 | PV | 23 | 238 | D | 163 | Clearance of drip loops of luminaries or traffic signal brackets | Conditions that could reasonably be expected to endanger life or property | Almost Always | 1. Road Widening 2. Forced Relocate 3. Scheduled Pole Replacement 4. Scheduled Rebuild 5. Scheduled Corrections | Yes (see code)
54 | PR | 23 | 239 | A | 165 | Loose Wire | Conditions that could reasonably be expected to endanger life or property | Almost Always | Never | Yes (see code)
55 | DB | 26 | 261 |  | 199 | Damage Equipment (including pole leaning) | Conditions that could reasonably be expected to endanger life or property | Almost Always | Never | None | Also see 214 (page 70) Table 261-1A (page 20) 420C2 (page 252)
56 | MS | 26 | 264 | A | 211 | Guying Needed | Conditions that could reasonably be expected to endanger life or property | Almost Always | Never
57 | PS | 26 | 264 | A | 211 | Loose Guying | Conditions that could reasonably be expected to endanger life or property | Almost Always | Never
58 | U | 31 | 311 | C | 220 | Ground laid service drops | Conditions that could reasonably be expected to endanger life or property | Almost Always | Never | None | Also see 014 (page 2)
OJUA DEVIATION CODE
| Code | Deviation
| AB | Abandoned
| BD | Building
| BH | Building/Horizontal clearance
| BV | Building/Vertical clearance
| DB | Damaged/Broken
| MH | Mid-span/Horizontal clearance
| MS | Missing
| MV | Mid-span/Vertical clearance
| OL | Out of Lead
| PC | Pole/Climbing/working space
| PG | Pole/Grounding | [6 empty] | Note: Any situation can become an immeditate hazard if it has
| PH | Pole/Horizontal clearance | [6 empty] | a high potential to result in additional rapid deteriaoration of the
| PL | Pole Leaning | [6 empty] | structural integrity or the electrical continuity of the system or
| PM | Pole/Marking | [6 empty] | results in encroachment in to the public space.
| PR | Pole/Riser
| PS | Pole/Structure
| PV | Pole/Vertical clearance
| U | Underground

## Abbreviations
Attachments |  | Violations
Attachment Type (Type) | Code | Equipment (EQUIP. 1 & 2) | Code | Equipment (continued) | Code | Suggested Action
Antennas | ANT | Anchor | ANC | Riser | RIS | Attach
Communication Cross-Connect | XBOX | Anchor (auxiliary) | AANC | Roof | ROOF | Attach Mid-span
Communication Drop | COMD | Antennas | ANT | Sidewalk Fixture | SWF | Bury
Communication Equipment (other) | CEO | Bridge | BR | Signs | SIGN | Contact Jump Pole
Communication Fiber-optic | COFO | Communication Bridle Wire | BWR | Stand Off Brackets | SOB | Ground/Bond
Communication Load Coil | LOAD | Communication Cross-Connect | XBOX | Stencils/Pole Tag | STN | Guard
Communication Mainline | COML | Communication C-Wire | CWR | Subscriber Network Interface | SNI | Lengthen
Communication Messenger | COMM | Communication Drop | COMD | Supply Fiber-optic | SPFO | Lower
Communication Power Supply | PS | Communication Equipment (other) | CEO | Traffic Signal Bracket | TRSB | Lower CATV
Communication Repeater | REP | Communication Fiber-optic | COFO | Traffic Signals | TRS | Lower Fiber
Communication Terminal | TRM | Communication Load Coil | LOAD | Trees/Vegetation | TREE | Lower Neutral
Conduit-metal | MCON | Communication Mainline | COML | U-Guard | UGRD | Lower Other
Conduit-PVC | CON | Communication Messenger | COMM | Inaccessible Surface | UNSR | Lower Power
Cross-arm | XARM | Communication Power Supply | PS | Water Surface | WSR | Lower Secondary
Cross-arm (fiberglass) | XARF | Communication Repeater | REP | Weather Head | WH | Lower Telco
Down Guy | GUY | Communication Terminal | TRM | Window | WIN | Make Ready
Fiber Equipment (other) | FEO | Conduit-metal | MCON | Wireless Equipment (other) | WEO | Move 1st attachment
Others Mainline | OTML | Conduit-PVC | CON |  |  | Move Mid-span
Others Messenger | OTMM | Cross-arm | XARM |  |  | Move to Span
Overhead Guy | OGUY | Cross-arm (fiberglass) | XARF |  |  | Place
Pedestal | PED | Cross-arm Braces | XARB | Base Pole Info |  | Place BSW (buried service wire)
Platform | PF | Curb | CURB | Timber Species (Material) | Code | Place California Top
Pole to Pole Guy | PPG | Down Guy | GUY | Douglas fir | DF | Place Clearance Pole
Power Meter | PMR | Drivable Surface | DRSR | Concrete | CC | Place Cross-arm
Power Neutral | NEUT | Fence | FENC | Fiberglass | FG | Place Mid-set Pole
Power Primary | PRI | Fiber Equipment (other) | FEO | Jack Pine | JP | Place Split Duct
Power Secondary | SEC | Fire Hydrant | HYD | Laminated | LM | Place Taller Pole
Power Service Drop | PDRP | Ground Rod | GRND | Lodgepole Pine | LP | Raise
Power Service Support Wire | PSSW | Ground Wire | GRWR | Metal/Steel | ST | Raise CATV
Power Street Light | SLT | Guy Marker | GM | Ponderosa Pine | WP | Raise Fiber
Power Switch | SWCH | Hardware | HDWR | Red Pine | NP | Raise Neutral
Power Transformer | XFMR | Insulator | INS | Southern Pine | SP | Raise Other
Private Party Attachment | PVT | Lashing Wire | LWR | Southern Yellow Pine | SYP | Raise Power
Riser | RIS | Multi-grounded Neutral | MGN | Western Larch | WL | Raise Secondary
Signs | SIGN | Others Mainline | OTML | Western Red Cedar | WC | Raise Telco
Stand Off Brackets | SOB | Others Messenger | OTMM |  |  | Refer to Engineering
Supply Fiber-optic | SPFO | Overhead Guy | OGUY |  |  | Relocate/Move
Traffic Signal Bracket | TRSB | Padmount Equipment | PAD |  |  | Remove
Traffic Signals | TRS | Pedestal | PED |  |  | Repair
Wireless Equipment (other) | WEO | Pedestrian Surface | PEDS | Base Pole Info |  | Replace
|  | Platform | PF | Directional Information | Abbrev. | Re-Tension
Violations |  | Pole | POLE | North | N | Shorten
Deviation Code (DEV.) | Code | Pole Step | STEP | South | S | Tighten
Abandoned | AB | Pole to Pole Guy | PPG | East | E | Transfer
Building | BD | Pole-Metal | MPOL | West | W | Trim
Building/Horizontal clearance | BH | Power Bracket | PBRK | North East | NE
Building/Vertical clearance | BV | Power Capacitor | PCAP | South East | SE
Damaged/Broken | DB | Power Drip-loop | PDLP | North West | NW
Mid-span/Horizontal clearance | MH | Power Jumpers | JUMP | South West | SW
Mid-span/Vertical clearance | MV | Power Mast | PMST | North Side | N/S
Missing | MS | Power Meter | PMR | South Side | S/S
Out of Lead | OL | Power Neutral | NEUT | East Side | E/S
Pole Leaning | PL | Power Primary | PRI | West Side | W/S
Pole/Climbing/working space | PC | Power Secondary | SEC | Field Side | F/S
Pole/Grounding | PG | Power Service Drop | PDRP | Road Side | R/S
Pole/Horizontal clearance | PH | Power Service Support Wire/Bridle | PSSW | North Of | N/O
Pole/Marking | PM | Power Street Light | SLT | South Of | S/O
Pole/Riser | PR | Power Switch | SWCH | East Of | E/O
Pole/Structure | PS | Power Transformer | XFMR | West Of | W/O
Pole/Vertical clearance | PV | Private Party Attachment | PVT | Rear Of | R/O
Underground | U | Railroad | RR | Across From | A/F